## Instructions
Jar Test Program
Instructions
Enter Data:
Enter jar test data into the DataEntry worksheet.
The StockSolutionHELP worksheet provides information on making stock solutions.
The JarSettingsHELP worksheet provides information on setting mixing speeds and settling times.
The results from individual jar tests can be saved to the Database worksheet by clicking on the Updata Database Button
found in the DataEntry worksheet.
Results from a previous jar test can be retrieved from the database by inputting the jar test date and number and clicking
on the Retrieve Button found in the DataEntry worksheet.
Jar Test Program
| FILE: | JarTest38.xls
| AUTHORS: | L. DeMers, K. Rakness, and B. Hegg
| COMPANY: | Process Applications, Inc.
| PURPOSE: | Spreadsheet to support jar testing
CONTRIBUTORS: J. Schulze (TNRCC), J. Roney (KYDOW), J. Williams (LDHH)
DATE MODIFIED: |  | MODIFICATIONS & BY WHOM:
1998-07-15 | LDD developed program for Franklin CTA.
1999-07-20 | LDD added comments for data entry cells
1999-07-27 | LDD modified per use at TNRCC IT session (corrected error in polymer aid calc, modified chart)
Worksheet is protected except for data entry cells. Worksheet can be unprotected to modify.
1999-08-02 | LDD added calculation of jar RPM based on water temperature and desired G value.
2000-06-12 | KLR added macro to update database and retrieve data from the database.
2000-06-19 | LDD modified settling time calcs to consider rectangular and circular basin configurations.
2001-05-25 | LDD added worksheets to calculation velocity gradients for different types of mixers.
2001-07-20 | LDD modified settling time calcs based on settling velocity with and without tube settlers.
2001-08-15 | LDD added velocity gradient calculations for walking beam flocculator.
2001-09-19 | LDD added rapid mix velocity gradient input and HELP buttons for mixing worksheets.
2001-12-04 | LDD corrected error in rpm calculation based on input G value.
2002-01-14 | LDD added flexibility to use either 1 L or 2 L jars for making stock solutions.
2003-03-18 | LDD added enhancements to the velocity gradient worksheets (provided by J. Schulze).
2003-03-18 | LDD added calibration data worksheet (provided by J. Roney).
2003-03-18 | LDD revised stock solution help screen to include additional information and consolidate calculations;
modifications also made to input screen.
2003-04-01 | LDD added head loss calculations to HydraulicMixHELP worksheet (provided by J. Williams).
2004-08-26 | LDD added flexibilty to stock solution table.
2005-05-09 | LDD corrected error in V^2/2g formula (in HydraulicMixHELP). Added two rapid mix segments.
2008-04-11 | LDD added updated calibration data worksheet and modified flow and volume inputs to be consistent.
Renamed file to JARTEST32.
2008-07-10 | LDD fixed hidden row in the HydraulicMix worksheet and corrected spelling errors in worksheets.
Added pictures and mixer clarification. Changed name to JARTEST33.
2009-08-03 | LDD added additional tables for hydraulic, turbine, and paddle mixing calculations. Modified calibratation
data collection forms. Changed name to JARTEST34.
2009-08-03 | LDD added NozzleMix worksheet for pump injection rapid mix applications. Enhancements made to
additional hydaulic input tables. Changed name to JARTEST35.
2010-02-18 | LDD corrected temperature cell reference error in 2nd and 3rd flocculation mix tables.
Added 3rd segment for rapid mix. Change to JARTEST36.
2010-06-30 | LDD added notes on plate settler concepts and corrected formula to determine settling distance in plates
or tubes (minor change).
2010-09-30 | LDD change name to JARTEST37. No changes other than those noted for 6/30/09.
2017-10-12 | LDD added flexibility to use either 1 or 2 L square jars for the testing. File name updated to JARTEST38.
Added section to determine equivalent G x T for rapid mix.
Added open channel flow friction losses calculations in hydraulic mix worksheet.
Model by: Process Applications, Inc. Fort Collins, CO 970-223-5787

## Lookup (hidden)
Jar Test Summary for Winchester WTP WTP
Step 1 - Enter plant background data. Enter data in cells with white background only.
Plant/Train Name | Date | Test No. | Test Time, hr:min |  | Test Date |  | Warning: Do not enter data
Winchester WTP | 2003-03-05 | 1 | 15:00 |  | Test No. |  | in this screen. It is used to
Water Source | Flow Rate (MGD) | Raw Turbidity | Water Temp (C) | Raw pH | Raw Alk. (mg/L) | Raw TOC (mg/L) | retrieve data from the database.
Kentucky River | 2.5 | 9.9 | 6 | 7.7 | 122 | 0
Chemical | Coagulant | Other Chemical 1 | Other Chemical 2 | Settled Turbidity | IFE Turbidity | Treated TOC (mg/L)
Name | Thermafloc | 0 | 0 | 0 | 0 | 0
Current Dose | 0 | 0 | 0
Step 2 - Enter jar test settings. Click Jar Settings HELP Button for guidance on setting parameters.
| Rapid Mix #1 | Rapid Mix #2 | Floc, Stage 1 | Floc, Stage 2 | Floc, Stage 3 | Settle Time (min)
Speed (RPM) | 80 | 0 | 52 | 15 | 0
Time (sec, min) | 100 | 0 | 14 | 14 | 0 | 15
Step 3 - Enter desired dose to determine volume of stock solution for each jar.
Click on Stock Solution HELP Button for guidance on preparing stock solutions.
Desired Stock | Coagulant | Other Chemical 1 | Other Chemical 2 | Raw Water Added to Jars (mL)
Solution Concentration (%) | 2 | 0 | 0 | 2000
Coagulant Jar # | 1 | 2 | 3 | 4 | 5 | 6
Coagulant Dose (mg/L) | 10 | 20 | 30 | 40 | 50 | 60
Stock Solution (mL) | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Other Chem. 1 Dose (mg/L) | 0 | 0 | 0 | 0 | 0 | 0
Stock Solution (mL)
Other Chem. 2 Dose (mg/L) | 0 | 0 | 0 | 0 | 0 | 0
Stock Solution (mL)
Step 4 - Conduct jar test and enter results below.
Jar Number | 1 | 2 | 3 | 4 | 5 | 6
Coagulant Dose (mg/L) | 0 | 0 | 0 | 0 | 0 | 0
Other Chemical 1 (mg/L) | 0 | 0 | 0 | 0 | 0 | 0
Other Chemical 2 (mg/L) | 0 | 0 | 0 | 0 | 0 | 0
Time to floc formation (min) | 0 | 0 | 0 | 0 | 0 | 0
Size of floc at mix end (mm) | 0 | 0 | 0 | 0 | 0 | 0
Settled Turbidity (NTU) | 10.2 | 4.2 | 3 | 3.2 | 0.8 | 1.45
Settled pH | 7.35 | 7.15 | 7.19 | 7.16 | 7.29 | 7.12
Filtered Turbidity (NTU) | 0 | 0 | 0 | 0 | 0 | 0
Settled TOC (mg/L) | 0 | 0 | 0 | 0 | 0 | 0
Filtered UV Absorb. (cm-1) | 0.0755 | 0.064 | 0.058 | 0.053 | 0.052 | 0.0445
TOC Removal, % | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
TOC Removal, %
|  |  |  | #N/A | #N/A
| retrievedatesample | 37685.01 |  | Inputdatetest | 0
| lookupdatesample | 37685.01 |  | lookupdatesample | #N/A
| CheckRetrieveDate | 1 |  | CheckDatabase | #N/A
Jar Settings HELP Button
Stock Solution HELP Button

## DataEntry
Jar Test Summary for WTP
Step 1 - Enter plant background data. Enter data in cells with white background only
Plant/Train Name | Date | Test No. | Test Time, hr:min |  | Test Date | 2003-03-05
[5 empty] | Test No. | 1
Water Source | Flow Rate (MGD) | Raw Turbidity | Water Temp (C) | Raw pH | Raw Alk. (mg/L) | Raw TOC (mg/L)
Chemical | Coagulant | Other Chemical 1 | Other Chemical 2 | Settled Turbidity | IFE Turbidity | Treated TOC (mg/L)
Name
Current Dose
Step 2 - Enter jar test settings. Click Jar Settings HELP Button for guidance on setting parameters.
| Rapid Mix #1 | Rapid Mix #2 | Floc, Stage 1 | Floc, Stage 2 | Floc, Stage 3 | Settle Time (min)
Speed (RPM)
Time (min)
Step 3 - Enter desired dose to determine volume of stock solution for each jar.
Click on Stock Solution HELP Button for guidance on preparing stock solutions.
Desired Stock | Coagulant | Other Chemical 1 | Other Chemical 2 | Raw Water Added to Jars (mL)
Solution Concentration (%)
Jar # | 1 | 2 | 3 | 4 | 5 | 6
Coagulant Dose (mg/L)
Stock Solution (mL)
Other Chem. 1 Dose (mg/L)
Stock Solution (mL)
Other Chem. 2 Dose (mg/L)
Stock Solution (mL)
Step 4 - Conduct jar test and enter results below.
Jar Number | 1 | 2 | 3 | 4 | 5 | 6
Coagulant Dose (mg/L) | 0 | 0 | 0 | 0 | 0 | 0
Other Chemical 1 (mg/L) | 0 | 0 | 0 | 0 | 0 | 0
Other Chemical 2 (mg/L) | 0 | 0 | 0 | 0 | 0 | 0
Time to floc formation (min)
Size of floc at mix end (mm)
Settled Turbidity (NTU)
Settled pH
Filtered Turbidity (NTU)
Settled TOC (mg/L)
Filtered UV Absorb. (cm-1)
TOC Removal, % | 0% | 0% | 0% | 0% | 0% | 0%
Note on F3: Use this button to retrieve historical data from the database.
Note on H3: Enter date jar test was performed
Note on C4: You must enter a date before the data can be posted to the database.
Note on E4: Enter time in military format but use a colon, for example, 9:30 PM can either be entered as 9:30 pm or 21:30.
Note on H4: Enter the number of the jar test (for example, 1)
Note on E6: Accurate mixing energy (G value) calculations require current water temperature entry.
Retrieve
Update Database Button
Stock Solution HELP Button
Jar Settings HELP Button

## StockSolutionsHELP
Stock Solution HELP Screen
The goal of this guideline is to help you "Prepare a Stock Solution"
Table 1: Determining the concentration of the stock solutions
To use Table 1, FIRST determine how much raw water you will be adding to each jar. For example, if you are using 2,000 mL jars and conducting a
conventional jar test, you will typically be adding 2,000 mL to each jar. SECOND, consider the chemical dosages that are to be added to each jar.
For example, you may want the alum dosage to increase by 10 mg/L in each jar. THIRD, identify the stock solution concentration (%) that you need
to prepare and transfer this information to Table 3 below.
Table 1
| How much raw water are you going to put in each jar? |  | 2000 | mL
| How much do you want the dosage (mg/L) |  | Concentration of the stock
| to change for each milliliter (mL) of stock solution |  | solution that you need to prepare
| that you add to a jar? |  | (%) | (Mg/L)
| 0.05 |  | 0.01 | 100
| 0.25 |  | 0.05 | 500
| 0.5 |  | 0.1 | 1000
| 1 |  | 0.2 | 2000
| 2.5 |  | 0.5 | 5000
| 5 |  | 1 | 10000
| 10 |  | 2 | 20000
| 15 |  | 3 | 30000
| 20 |  | 4 | 40000
|  |  | 0 | 0
The following equation is used to calculate the Stock Solution Concentration in Table 1:
Stock Solution Concentration (%) =
Desired Dosage (mg/L) x Volume of Raw Water (mL)
Amount of Stock Solution added to each jar (1 mL) x 10,000 (mg/L to % conversion factor)
Table 2: Determining the product strength of liquid chemicals
To determine how much liquid chemical you must use to prepare the stock solution, you must first determine the product strength. Product strength
is the actual (reactive) chemical that is contained in each gallon of liquid. To determine the product strength, you must know the product specific
gravity and percent concentration. For example, liquid alum has a product specific gravity of 1.35 and a percent concentration of about 48 %.
Product specific gravity and percent concentration can be determined from the product supplier and product information sources such as MSDS.
Once the product specific gravity and percent concentration are known, Table 2 can be used to determine the product strength.
Table 2
|  | Coagulant | Other Chemical 1 | Other Chemical 2
Product Strength (%)
Specific Gravity
Product Strength (lb/gal)
Table 3: Making the stock solution
Table 3
Step 1 - Select desired stock solution concentration from Table 1 above
| Desired Stock | Coagulant | Other Chemical 1 | Other Chemical 2
Solution Concentration (%)
Step 2 - Determine amount of product to add to flask of indicated size
If product is a DRY
| Parameter | Coagulant | Other Chemical 1 | Other Chemical 2
Flask size (mL)
Product Purity, %
| Weight to add to flask, gm | 0 | 0 | 0 | 0
If product is LIQUID
| Parameter | Coagulant | Other Chemical 1 | Other Chemical 2
Flask size (mL)
Product Strength, lb/gal
| Volume to add to flask, mL | 0 | 0 | 0 | 0
The following equation is used to determine the product volume:
| Product volume (mL) = | (% solution) x (flask volume, mL) x (8.34 lb/gal)
100 x (product strength, lb/gal)
Return to Data Entry Screen
Return to Data Entry Screen
Note on E11: Typically, this will be the volume of the jars that you are using. If you are mixing sludge and raw water in a jar, the raw water volume will be less than the jar capacity.
Note on D60: Input known product strength or calculated value from Table 2.
Note on E60: Input known product strength or calculated value from Table 2.
Note on F60: Input known product strength or calculated value from Table 2.

## Calculate (hidden)
[13 empty] | Current | Other | Current Dose | Other | Current Dose |  |  |  | Rapid Mix | Rapid Mix | Rapid Mix | Rapid Mix | Floc | Floc | Floc | Floc | Floc | Floc |  | Stock Solution Concentration |  |  | Raw Water | Jar 1 | Jar 1 | Jar 1 | Jar 1 | Jar 1 | Jar 1 | Jar 1 | Jar 1 | Jar 1 | Jar 1 | Jar 2 | Jar 2 | Jar 2 | Jar 2 | Jar 2 | Jar 2 | Jar 2 | Jar 2 | Jar 2 | Jar 2 | Jar 3 | Jar 3 | Jar 3 | Jar 3 | Jar 3 | Jar 3 | Jar 3 | Jar 3 | Jar 3 | Jar 3 | Jar 4 | Jar 4 | Jar 4 | Jar 4 | Jar 4 | Jar 4 | Jar 4 | Jar 4 | Jar 4 | Jar 4 | Jar 5 | Jar 5 | Jar 5 | Jar 5 | Jar 5 | Jar 5 | Jar 5 | Jar 5 | Jar 5 | Jar 5 | Jar 6 | Jar 6 | Jar 6 | Jar 6 | Jar 6 | Jar 6 | Jar 6 | Jar 6 | Jar 6 | Jar 6
Date & |  | Plant/Train | Water | Test | Test | Raw | Water | Water | Raw | Raw | Raw | Coagulant | Dose | Chemical 1 | Other | Chemical 2 | Other | Settled | IFE | Finished | Speed | Speed | Speed | Speed | Stage 1 | Stage 1 | Stage 2 | Stage 2 | Stage 3 | Stage 3 | Settle | Coagulant | Other | Other | Added to | Coagulant | Other Chem 1 | Other Chem 2 | Time to Floc | Floc | Settled | Settled | Filtered | Settled | Settled | Coagulant | Other Chem 1 | Other Chem 2 | Time to Floc | Floc | Settled | Settled | Filtered | Settled | Settled | Coagulant | Other Chem 1 | Other Chem 2 | Time to Floc | Floc | Settled | Settled | Filtered | Settled | Settled | Coagulant | Other Chem 1 | Other Chem 2 | Time to Floc | Floc | Settled | Settled | Filtered | Settled | Settled | Coagulant | Other Chem 1 | Other Chem 2 | Time to Floc | Floc | Settled | Settled | Filtered | Settled | Settled | Coagulant | Other Chem 1 | Other Chem 2 | Time to | Floc | Settled | Settled | Filtered | Settled | Settled | Last
Sample No. | Date | Name | Source | No. | Time | Turbidity | Temperature | Flow | pH | TOC | Alkalinity | Name | Coagulant | Name | Chemical 1 | Name | Chemical 2 | Turbidity | Turbidity | TOC | #1 | #1 | #2 | #2 | Speed | Time | Speed | Time | Speed | Time | Time |  | Chemical 1 | Chemical 2 | Jars | Dose | Dose | Dose | Formation | Size | Turb | pH | Turb | TOC | UV absorb | Dose | Dose | Dose | Formation | Size | Turb | pH | Turb | TOC | UV absorb | Dose | Dose | Dose | Formation | Size | Turb | pH | Turb | TOC | UV absorb | Dose | Dose | Dose | Formation | Size | Turb | pH | Turb | TOC | UV absorb | Dose | Dose | Dose | Formation | Size | Turb | pH | Turb | TOC | UV absorb | Dose | Dose | Dose | Floc | Size | Turb | pH | Turb | TOC | UV absorb | Column
# | m/d/y |  |  | # | hr:min | NTU | C | MGD | units | mg/L | mg/L | [9 empty] | RPM | min | RPM | min | RPM | min | RPM | min | RPM | min | min | % | % | % | mL | mg/L | mg/L | mg/L | min | mm | NTU | units | NTU | mg/L | cm-1 | mg/L | mg/L | mg/L | min | mm | NTU | units | NTU | mg/L | cm-1 | mg/L | mg/L | mg/L | min | mm | NTU | units | NTU | mg/L | cm-1 | mg/L | mg/L | mg/L | min | mm | NTU | units | NTU | mg/L | cm-1 | mg/L | mg/L | mg/L | min | mm | NTU | units | NTU | mg/L | cm-1 | mg/L | mg/L | mg/L | min | mm | NTU | units | NTU | mg/L | cm-1
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97
0 | 0 | 0 | 0 | 0 | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## JarG
G calculations for jar testing
|  |  | Impller: 1 inch x 3 inch (25.4 mm x 76 mm) |  |  |  | 1930.4 |  |  |  |  | Impeller: 40 mm x 60 mm |  |  | 2400
| Input 2 liter jar: | [8 empty] | Input 1 liter jar based on EC Engineering design and mixing curve.
Diameter | D | 0.24606 | ft | [5 empty] | Diameter | D | 0.25262 | ft | 7.7 cm versus 6 cm to match vendor curve
| Np | 3 | FBT | Adjusted from recommended value of 3.6 for flat blade turbine to fit original curve | [5 empty] | Np | 3 | FBT
Specific gravity | S | 1 | [6 empty] | Specific gravity | S | 1
Volume | V | 0.070642 | ft3 | [5 empty] | Volume | V | 0.035321 | ft3
Viscosity | u | 3.746e-05 | lb-sec/ft2 @ 0C | [6 empty] | u | 3.746e-05 | lb-sec/ft2 @ 0C
| u | 3.229e-05 | lb-sec/ft2 @ 4C | [6 empty] | u | 3.229e-05 | lb-sec/ft2 @ 4C
| u | 2.735e-05 | lb-sec/ft2 @ 10C | [6 empty] | u | 2.735e-05 | lb-sec/ft2 @ 10C
| u | 2.359e-05 | lb-sec/ft2 @ 16C | [6 empty] | u | 2.359e-05 | lb-sec/ft2 @ 16C
| u | 2.05e-05 | lb-sec/ft2 @ 21C | [6 empty] | u | 2.05e-05 | lb-sec/ft2 @ 21C
| u | 1.799e-05 | lb-sec/ft2 @ 27C | [6 empty] | u | 1.799e-05 | lb-sec/ft2 @ 27C
| u | 1.595e-05 | lb-sec/ft2 @ 32C | [6 empty] | u | 1.595e-05 | lb-sec/ft2 @ 32C
|  | Temperature C | [7 empty] | Temperature C
| RPM | 0 | 4 | 10 | 16 | 21 | 27 | 32 | RPM | 0 | 4 | 10 | 16 | 20 | 27 | 32
| 10 | 3.0316 | 3.2653 | 3.5479 | 3.8202 | 4.098 | 4.3746 | 4.6459 | 10 | 4.5788 | 4.9318 | 5.3587 | 5.77 | 6.1896 | 6.6073 | 7.0171
| 30 | 15.7525 | 16.9667 | 18.4355 | 19.8504 | 21.2939 | 22.7309 | 24.1408 | 30 | 23.7924 | 25.6264 | 27.8447 | 29.9818 | 32.1621 | 34.3325 | 36.462
| 50 | 33.8939 | 36.5066 | 39.6668 | 42.7112 | 45.8172 | 48.9092 | 51.9428 | 50 | 51.193 | 55.1392 | 59.9123 | 64.5105 | 69.2018 | 73.8718 | 78.4538
| 100 | 95.8665 | 103.2563 | 112.1946 | 120.8055 | 129.5907 | 138.336 | 146.9164 | 100 | 144.7957 | 155.9572 | 169.4575 | 182.4633 | 195.7323 | 208.9411 | 221.9009
| 300 | 498.1369 | 536.5357 | 582.9804 | 627.7239 | 673.373 | 718.8149 | 763.4002 | 300 | 752.3803 | 810.3773 | 880.5269 | 948.1069 | 1017.0548 | 1085.6897 | 1153.0309
Water Viscosity Table
[6 empty] | 0 | 3.746e-05
[6 empty] | 4.4 | 3.229e-05
[6 empty] | 10 | 2.735e-05
| Temperature | Trend Visc. |  |  |  | 15.6 | 2.359e-05
| 0 | 3.7125e-05 |  |  |  | 21.1 | 2.05e-05
[6 empty] | 26.7 | 1.799e-05
[6 empty] | 32.2 | 1.595e-05

## JarSettingsHELP
Jar Settings HELP Screen
Step 1 - Determine rapid mix time based on available rapid mix volume and flow rate through rapid mix. To determine the mixing
energy (G value), use plant design info or refer to HELP buttons for type of mixing.
| Enter square jar volume (1 or 2) |  | Liters
| 1 or 2 Liter | [5 empty] | When G value exceeds G achievable by jar @ 300 rpm, equivalent G x t can be used to adjust mixing time.
Stage | 1st | 2nd | 3rd
Rapid Mix Volume (ft3) | [7 empty] | 1st Stage |  | 3rd Stage
Rapid Mix Flow Rate (MGD) | [7 empty] | Full Scale | Jar @ 300 rpm | Full Scale | Jar @ 300 rpm
Mix Time (sec) | CALCULATION | CALCULATION | CALCULATION |  |  |  | Time, sec | CALCULATION | #VALUE! | CALCULATION | #VALUE!
G Value (sec-1) | [6 empty] | G, sec-1 | 0 | 600 | 0 | 600
Jar RPM | CALCULATION | CALCULATION | CALCULATION |  |  |  | G x t | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Step 2 - Determine flocculation time per stage based on available flocculation volume and flow rate through the flocculation stage.
To determine mixing energy (G value) for each stage, use plant design info or refer to HELP buttons for type of mixing.
Table 3 | [6 empty] | Additional transition segments
STAGE | 1st | 2nd | 3rd | 4th | Hydraulic & Turbine Mix buttons |  | Floc In | Sed In
Volume (ft3) |  |  |  |  | may also apply to flocculation
Flow Rate (MGD)
Floc Time (min) | CALCULATION | CALCULATION | CALCULATION | CALCULATION |  |  | CALCULATION | CALCULATION
G Value (sec-1)
Jar RPM | CALCULATION | CALCULATION | CALCULATION | CALCULATION |  |  | CALCULATION | CALCULATION
Step 3 - Determine the jar settling time based on the sed basin surface overflow rate (rise rate) and corresponding particle settling
velocity. If the sed basins have tube settlers installed, use input box on the right.
|  |  |  | Conventional Basin with Tube or Plate Settlers | [8 empty] | Plate opening (typ. 5 cm)
Conventional Basin |  |  |  | Tube or Plate Opening (inch)
Flow Rate (MGD) |  |  |  | Tube or Plate Angle (degrees) |  |  | 0 | rise rate (ft/min)
Surface Area (ft2) |  |  |  | Tube or Plate Depth (inch) |  |  | 0 | tube velocity (ft/min)
Settling velocity (cm/min) |  | CALCULATION |  | Flow Rate (MGD) |  |  | 0 | tube path length (ft) |  |  |  |  | Plate angle (typ. 60 degrees)
Floc to Sed Transition Time - (min) |  |  |  | Surface Area (ft2) |  |  | 0 | tube dt (min)
Jar Settling Time * (min) |  | CALCULATION |  | Settling Velocity (cm/min) |  | CALCULATION | 0 | tube settling distance (cm) |  |  |  | plate settling distance = plate opening / cos plate angle
* Based on 10 cm sample depth in jar |  |  |  | Floc to Sed Transition Time - (min)
|  |  |  | Sample Time (min) |  | CALCULATION
Hydraulic Mix HELP Button
Turbine Mix HELP Button
Return to Data Entry Screen
Paddle Mix HELP Button
Walking Beam Mix HELP Button
Nozzle Mix HELP Button
Note on D11: Enter mixing energy (G) for rapid mix
Note on E11: Enter mixing energy (G) for rapid mix
Note on F11: Enter mixing energy (G) for rapid mix
Note on N11: G value at 300 rpm
Note on D22: Enter mixing energy (G) for 1st stage
Note on E22: Enter mixing energy (G) for 2nd stage
Note on F22: Enter mixing energy (G) for 3rd stage
Note on G22: Enter mixing energy (G) for 4th stage
Note on D23: Correct RPM requires water temperature input (cell E6; DataEntry)
Note on E23: Correct RPM requires water temperature input (cell E6; DataEntry)
Note on F23: Correct RPM requires water temperature input (cell E6; DataEntry)
Note on G23: Correct RPM requires water temperature input (cell E6; DataEntry)
Note on L23: Correct RPM requires water temperature input (cell E6; DataEntry)
Note on M23: Correct RPM requires water temperature input (cell E6; DataEntry)
Note on G29: Distance between parallel tubes or plates
Note on I29: Enter tube opening (typ. ~ 2 inch); for plate, distance between plate
Note on I30: Enter tube or plate angle (typ. 60 degrees for tubes)
Note on E31: Enter total surface area of sed basins
Note on I31: Enter tube or plate vertical depth
Note on E33: Enter time following flocculation for jars to become quiescent (estimated 0.5 to 2 minutes)
Note on I33: Enter area of tube settlers or plates
Note on I35: Enter time following flocculation for jars to become quiescent (estimated 0.5 to 1 minutes)

## Calibrate Data
Jar Test Calibration Parameters
Chemicals added at Rapid Mix
Parameter | Chemical 1 | Chemical 2 | Chemical 3 | Chemical 4
Liquid (description)
Specific gravity
Product strength, %
Product strength, lb/gal
Dry (description)
Product purity, %
Comments/Notes:
Rapid Mix (collect data for appropriate configuration)
Hydraulic Mixing Stage | Segment 1 with nozzles | Segment 2 with no nozzles | Segment 3 with nozzles
Basin or pipe dimensions
Basin or pipe volume, ft3
Head loss across basin/pipe, ft
Turbine Mixing Stage
Blade diameter (tip to tip), ft
Description of blade1
Basin volume, ft3
Turbine speed (actual and max), rpm
Comments/Notes (include length and diameter of pipe, # bends if used as rapid mix): Nozzle mixing system
Jar Test Calibration Parameters (Page 2)
Flocculator (collect data for appropriate configuration)
Note: If using multiple stage flocculation, determine information for each stage.
Turbine Mixing Stage | 1st | 2nd | 3rd | 4th
Basin dimensions
Description of blade1
Blade diameter (tip to tip), ft
Basin volume, ft3
Turbine speed (actual and max), rpm
Paddle Mixing Stage
Area of paddles (L x W x No. paddles), ft2
Diameter of paddles (tip to tip), ft
Basin volume, ft3
Paddle speed (actual and max), rpm
Walking Beam Stage
Area of paddles (L x W x No. paddles), ft2
Paddle stroke length, ft
Basin volume, ft3
Paddle speed (actual and max), rpm
Comments/Notes:
Sedimentation (collect data for appropriate configuration)
Without Tubes
Surface area, ft2
With Tubes
Tube opening, inches
Tube angle, degrees
Tube depth, inches
Area covered by tubes, ft2
Comments/Notes:
1 See Turbine Mix Help worksheet

## HydraulicMixHELP
Calculation of Velocity Gradient (G) for Hydraulic Mixing
Parameters | Input | Input | Input | Input | Units
Description
Basin/Pipe Volume |  |  |  |  | ft3
Flow Rate |  |  |  |  | MGD
Head loss (hL) |  |  |  |  | ft | Note: Headloss through piping segments can be estimated
Weight of Fluid (w) | 62.4 | 62.4 | 62.4 | 62.4 | lb/ft3
Water Temperature | 0 | 0 | 0 | 0 | C
Dynamic viscosity (u) | 3.7125e-05 | 3.7125e-05 | 3.7125e-05 | 3.7125e-05 | lb-sec/ft2
Velocity Gradient (G) | 0 | 0 | 0 | 0 | sec-1 | by paging down and using the Hazen-Williams input box.
Note: Input current water temperature in the DataEntry Screen.
The velocity gradient calculation requires a current value to be accurate.
Transfer the velocity gradient value to the JarSettingsHELP worksheet.
The Hazen-Williams equation for determination of head loss in pressure pipe (should be used only for turbulent flow).
Input
Flow (MGD) =
Pipe Diameter (inches) =
Length (feet) =
C =
Calculations
Q (gpm) = | 0
| 0 | [5 empty] | Velocity Head | ft | 0.0061144
A (sf) = | 0
V (fps) = | #DIV/0!
S = | #DIV/0!
Head loss - friction (ft) = | #DIV/0!
Pressure head (psi) = | #DIV/0!
Should minor losses be considered? | NO
V^2/2g = | #DIV/0!
K factors for minor losses |  | HL (ft)
90o bend | 0.3 | #DIV/0!
Squared edged inlet | 0.5 | #DIV/0!
Inward projecting pipe | 1 | #DIV/0!
Hazen-Williams Coefficient
Water Supply and Pollution Control, 4th ed., Viessman and Hammer, 1985
Pipe Material | C
New cast iron | 130
5-yr-old iron | 120
20-yr-old cast iron | 100
Average concrete | 130
New welded steel | 120
Asbestos cement | 140
Plastic | 150
The Manning equation for determination of head loss in open channel flow (should be used only for turbulent flow).
ISCO Open Channel Flow Measurement Handbook p. 67
Parameters | Input | Input |  | Input | Units
Description
Width |  |  |  |  | ft
Height |  |  |  |  | ft
Length |  |  |  |  | ft
Channel area | 0 | 0 |  | 0 | ft^2
Channel wettted perimeter | 0 | 0 |  | 0 | ft
Channel hydraulic diameter | #DIV/0! | #DIV/0! |  | #DIV/0! | ft
Flow rate |  |  |  |  | MGD
Flow rate | 0 | 0 |  | 0 | ft^3/sec
Viscosity of water - µ | 3.7125e-05 | 3.7125e-05 |  | 3.7125e-05 | lb-sec/ft2
n for concrete
Channel hydraulic slope | #DIV/0! | #DIV/0! |  | #DIV/0!
Channel friction loss due to flow | #DIV/0! | #DIV/0! |  | #DIV/0! | ft
Minor loss
Opening Height |  |  |  |  | ft
Opening Width |  |  |  |  | ft
Flow rate through opening |  |  |  |  | ft^3/sec
Velocity | #DIV/0! | #DIV/0! |  | #DIV/0! | ft/sec
Minor loss due to opening | #DIV/0! | #DIV/0! |  | #DIV/0! | ft
Minor loss
Opening Height |  |  |  |  | ft
Opening Width |  |  |  |  | ft
Flow rate through opening |  |  |  |  | ft^3/sec
Velocity |  |  |  | #DIV/0! | ft/sec
Minor loss due to opening |  |  |  | #DIV/0! | ft
Total losses | #DIV/0! | #DIV/0! |  | #DIV/0!
Return to Jar Settings HELP Screen
Return to Data Entry Screen
Note on B7: For open basins, input change in water elevation. Between inlet and outlet. For pipeline flow, use equation below to estimate head loss.
Note on C23: See table below for C values
Note on C32: Pipeline lengths in excess of 500 diameters are usually classified as long. Minor losses can be ignored for "long" pipelines. (1)

## NozzleMixHELP
Calculation of Velocity Gradient (G) for Pump Injection thru Nozzle
Parameters | Input |  | Units
Description
Coefficient of discharge |  |  |  | 0.85 | Obtained from Tacoma jar test speadsheet
Area of nozzle |  |  | ft2 | 0.375 | inch dia nozzle
Flow rate through nozzle |  |  | gpm | 0.03125 | ft dia nozzle
Diameter of pipeline or area of flow |  |  | ft2 | 0.00076699 | ft^2 area for 1 nozzle
Jet velocity | #DIV/0! | #DIV/0! | ft/sec | 0.055223 | ft^2 area for 72 nozzles
Water horsepower | #DIV/0! | #DIV/0! | Hp
Mixing zone length |  |  | ft | See design below
Mixing volume | 0 | 0 | ft3
Weight of Fluid (w) | 62.4 | 62.4 | lb/ft3
Water temperature | 0 | 0 | C
Dynamic viscosity (u) | 3.7125e-05 | 3.7125e-05 | lb-sec/ft2
Velocity gradient (G) | 0 | 0 | sec-1
Flow rate |  |  | MGD
Detention time | #DIV/0! | #DIV/0! | sec
G x T | #DIV/0! | #DIV/0!
Note: Input current water temperature in the DataEntry Screen.
The velocity gradient calculation requires a current value to be accurate.
Transfer the velocity gradient value to the JarSettingsHELP worksheet.
Source: Tacoma WTP Jar Testing Spreadsheet
Time for Flash Mixing
The time for flash mixing is calculated based on the area in which mixing occurs. Mixing occurs across the channel for the length x, which can be found by: Time to Flash mix is found by: Where v = velocity of flow in channel Flash mix dimensions can be found on drawing 5M-7
Plan View
[6 empty] | Mixing zone x = | 2.309 | feet
Return to Jar Settings HELP Screen
Return to Data Entry Screen
𝑡𝑎𝑛30=𝑑/𝑥
𝑇𝑖𝑚𝑒=𝑥/𝑣
60°
60°
60°
30°
30°
d = 16"
d = 16"
60°
x
Note on C5: Typical value for coefficient of discharge is 0.75.
Note on D5: Typical value for coefficient of discharge is 0.75.
Note on C6: Area of the inner orifice of nozzle.
Note on D6: Area of the inner orifice of nozzle.
Note on C7: Obtain from pump curve or estimate at 3 % of design flow rate.
Note on D7: Obtain from pump curve or estimate at 3 % of design flow rate.
Note on C11: Mixing zone length estimated at 1.5 times the pipe diameter.

## TurbineMixHELP
Calculation of Velocity Gradient (G) for Vertical Turbine Mixers
Parameters |  | Input | Units | Note:
Description |  |  |  | Input current water temperature in the DataEntry screen - the
Blade Diameter (D) |  |  | ft | velocity gradient calculation requires a current value to be accurate.
Impeller Number (Np) |  |  | See Below
Volume (V) |  |  | ft3
Weight of Fluid (w) |  | 62.4 | lb/ft3
Acceleration of Gravity |  | 32.2 | ft/sec2
Water Temperature |  | 0 | C
Dynamic viscosity (u) |  | 3.7125e-05 | lb-sec/ft2
Controller Setting (%) |  | RPM (R) | G @ 0 C
Min | 0% | 0
10%
20%
30%
40%
50%
60%
70%
80%
90%
Max | 100%
Actual
NOTE:
Source of information, equations, and images: Mixing in Coagulation and Flocculation, AWWARF 1991 & |  |  |  |  | You will need to enter the data for each vertical turbine mixer
Water Works Engineering, Qasim & Zhu, Prentice Hall PTR 2000 |  |  |  |  | and then transfer the resulting G value to the appropriate box
in the JarSettingsHELP screen. For example, if the plant has a
Impeller Power Number (Np) |  |  |  |  | two-stage mixer, the table will need to be filled out for each stage.
Propeller Type |  |  | Np |  | Page down for additional turbine mixer data entry tables.
Flat Blade Turbine (radial flow) |  |  | 2.6 - 3.6
Disk Turbine (radial flow) |  |  | 5.1 - 6.2
Curved Blade Turbine (radial flow) |  |  | 2.5
45o Pitched Blade Turbine (axial flow) |  |  | 1.36 - 1.94
4-Blade Hydrofoil |  |  | 0.4
3-Blade Hydrofoil |  |  | 0.3
Propeller (axial flow) |  |  | 0.3 - 0.7
Flat blade turbine
Parameters |  | Input | Units
Description
Blade Diameter (D) |  |  | ft
Impeller Number (Np) |  |  | See Below
Volume (V) |  |  | ft3
Weight of Fluid (w) |  | 62.4 | lb/ft3
Acceleration of Gravity |  | 32.2 | ft/sec2
Water Temperature |  | 0 | C
Dynamic viscosity (u) |  | 3.7125e-05 | lb-sec/ft2
Controller Setting (%) |  | RPM (R) | G @ 0 C
Min | 0% | 0
10%
20%
30%
40%
50%
60%
70%
80%
90%
Max | 100%
Actual
Parameters |  | Input | Units
Description
Blade Diameter (D) |  |  | ft
Impeller Number (Np) |  |  | See Below
Volume (V) |  |  | ft3 | 19745
Weight of Fluid (w) |  | 62.4 | lb/ft3
Acceleration of Gravity |  | 32.2 | ft/sec2
Water Temperature |  | 0 | C
Dynamic viscosity (u) |  | 3.7125e-05 | lb-sec/ft2
Controller Setting (%) |  | RPM (R) | G @ 0 C
Min | 0% | 0
10%
20%
30%
40%
50%
60%
70%
80%
90%
Max | 100%
Actual
3-Blade Hydrofoil
Return to Jar Settings HELP Screen
Return to Data Entry Screen
Disk
Note on D6: Enter impeller number from table below based on type.
Note on D7: Enter the volume of individual chamber/stage in the rapid mix or flocculator.
Note on C14: Enter the lowest setting that you can use on your mixer's controller. (We have shown the units as "%" but if the units on your controller are just numbers, just enter the lowest number . . . It doesn't have to be in "%".)
Note on D14: Enter the minimum speed (in RPM) of the mixer that exists when the controller is set at its lowest setting.
Note on C24: Enter the highest setting that you can use on your mixer's controller. (We have shown the units as "%" but if the units on your controller are just numbers, just enter the highest number . . . It doesn't have to be in "%".)
Note on D24: Insert the maximum speed (in RPM) of the mixer that exists when the controller is set at its highest setting.
Note on C25: Enter the current setting of the mixer controller. (We have shown the units as "%" but if the units on your controller are just numbers, just enter the highest number . . . It doesn't have to be in "%".)
Note on D67: Enter impeller number from table below based on type.
Note on D68: Enter the volume of individual chamber/stage in the rapid mix or flocculator.
Note on C75: Enter the lowest setting that you can use on your mixer's controller. (We have shown the units as "%" but if the units on your controller are just numbers, just enter the lowest number . . . It doesn't have to be in "%".)
Note on D75: Enter the minimum speed (in RPM) of the mixer that exists when the controller is set at its lowest setting.
Note on C85: Enter the highest setting that you can use on your mixer's controller. (We have shown the units as "%" but if the units on your controller are just numbers, just enter the highest number . . . It doesn't have to be in "%".)
Note on D85: Insert the maximum speed (in RPM) of the mixer that exists when the controller is set at its highest setting.
Note on C86: Enter the current setting of the mixer controller. (We have shown the units as "%" but if the units on your controller are just numbers, just enter the highest number . . . It doesn't have to be in "%".)
Note on D92: Enter impeller number from table below based on type.
Note on D93: Enter the volume of individual chamber/stage in the rapid mix or flocculator.
Note on C100: Enter the lowest setting that you can use on your mixer's controller. (We have shown the units as "%" but if the units on your controller are just numbers, just enter the lowest number . . . It doesn't have to be in "%".)
Note on D100: Enter the minimum speed (in RPM) of the mixer that exists when the controller is set at its lowest setting.
Note on C110: Enter the highest setting that you can use on your mixer's controller. (We have shown the units as "%" but if the units on your controller are just numbers, just enter the highest number . . . It doesn't have to be in "%".)
Note on D110: Insert the maximum speed (in RPM) of the mixer that exists when the controller is set at its highest setting.
Note on C111: Enter the current setting of the mixer controller. (We have shown the units as "%" but if the units on your controller are just numbers, just enter the highest number . . . It doesn't have to be in "%".)

## PaddleMixHELP
Calculation of Velocity Gradient (G) for Paddle-Type Mixers
| Parameters | Input | Units | NOTE:
| Description |  |  | Input current water temperature in the DataEntry Screen - the
| Coefficient of Drag (Cd) |  |  | velocity gradient calculation requires a current value to be accurate.
| Area of Paddles (A) |  | ft2
| Diameter of Flocculator (d) |  | ft
| Volume of basin (V) |  | ft3
| Water Temperature | 0 | C
| u | 3.7125e-05 | lb-sec/ft2 @ 40F
Controller Setting (%) |  | RPM (R) | G @ 0 C
Min | 0% | 0
10%
20%
30%
40%
50%
60%
70%
80%
90%
Max | 100%
Actual
Source: Mixing in Coagulation and Flocculation, AWWARF 1991
NOTE:
You will need to enter the data for each paddle-type mixer
and then tranfer the resulting G value to the appropriate
box on the JarSettingsHELP screen. For example,
if the plant has three-stage mixer, the table will
need to be filled out once for each stage.
Page down for additional paddle-type mixer data entry tables.
Typical horizontal paddle-type flocculator
| Parameters | Input | Units
Description
Coefficient of Drag (Cd)
| Area of Paddles (A) |  | ft2
| Diameter of Flocculator (d) |  | ft
| Volume of basin (V) |  | ft3
| Water Temperature | 0 | C
| u | 3.7125e-05 | lb-sec/ft2 @ 40F
Controller Setting (%) |  | RPM (R) | G @ 0 C
Min | 0% | 0
10%
20%
30%
40%
50%
60%
70%
80%
90%
Max | 100%
Actual
| Parameters | Input | Units
Description
Coefficient of Drag (Cd)
| Area of Paddles (A) |  | ft2
| Diameter of Flocculator (d) |  | ft
| Volume of basin (V) |  | ft3
| Water Temperature | 0 | C
| u | 3.7125e-05 | lb-sec/ft2 @ 40F
Controller Setting (%) |  | RPM (R) | G @ 0 C
Min | 0% | 0
10%
20%
30%
40%
50%
60%
70%
80%
90%
Max | 100%
Actual
Return to Jar Settings HELP Screen
Return to Data Entry Screen
Note on D5: Typical value for flat paddle is 1.8
Note on D6: Enter total area of flocculator paddles in stage
Note on D8: Enter volume of floccuation stage
Note on C13: Enter the lowest setting that you can use on your mixer's controller. (We have shown the units as "%" but if the units on your controller are just numbers, just enter the lowest number . . . It doesn't have to be in "%".)
Note on D13: Enter the minimmum speed (in RPM) of the mixer that exists when the controller is set at its lowest setting.
Note on D23: Insert the maximum speed (in RPM) of the mixer that exists when the controller is set at its highest setting.
Note on C24: Enter the current setting of the mixer controller. (We have shown the units as "%" but if the units on your controller are just numbers, just enter the highest number . . . It doesn't have to be in "%".)
Note on D54: Typical value for flat paddle is 1.8
Note on D55: Enter total area of flocculator paddles in stage
Note on D57: Enter volume of floccuation stage
Note on C62: Enter the lowest setting that you can use on your mixer's controller. (We have shown the units as "%" but if the units on your controller are just numbers, just enter the lowest number . . . It doesn't have to be in "%".)
Note on D62: Enter the minimmum speed (in RPM) of the mixer that exists when the controller is set at its lowest setting.
Note on D72: Insert the maximum speed (in RPM) of the mixer that exists when the controller is set at its highest setting.
Note on C73: Enter the current setting of the mixer controller. (We have shown the units as "%" but if the units on your controller are just numbers, just enter the highest number . . . It doesn't have to be in "%".)
Note on D78: Typical value for flat paddle is 1.8
Note on D79: Enter total area of flocculator paddles in stage
Note on D81: Enter volume of floccuation stage
Note on C86: Enter the lowest setting that you can use on your mixer's controller. (We have shown the units as "%" but if the units on your controller are just numbers, just enter the lowest number . . . It doesn't have to be in "%".)
Note on D86: Enter the minimmum speed (in RPM) of the mixer that exists when the controller is set at its lowest setting.
Note on D96: Insert the maximum speed (in RPM) of the mixer that exists when the controller is set at its highest setting.
Note on C97: Enter the current setting of the mixer controller. (We have shown the units as "%" but if the units on your controller are just numbers, just enter the highest number . . . It doesn't have to be in "%".)

## BeamMixHELP
Calculation of Velocity Gradient (G) for Walking Beam Mixers
| Parameters | Input | Units | NOTE:
| Coefficient of Drag (Cd) | 3 |  | Input current water temperature in the DataEntry screen - the
| Area of Paddles (A) |  | ft2 | velocity gradient calculation requires a current value to be accurate.
| Paddle Stroke Length (L) |  | ft
| Volume of basin (V) |  | ft3
| Water Temperature | 0 | C
| u | 3.7125e-05 | lb-sec/ft2 @ 40F
| Controller Setting (%) | RPM (R) | G @ 0 C
Min | 0%
10%
20%
30%
40%
50%
60%
70%
80%
90%
Max | 100%
Actual
Source: Mixing in Coagulation and Flocculation, AWWARF 1991
NOTE:
You will need to enter the data for each walking-beam mixer
and then tranfer the resulting G value to the appropriate
box on the JarSettingsHELP screen. For example,
if the plant has three-stage flocculation, the table will
need to be filled out once for each stage.
Return to Data Entry Screen
Return to Jar Settings HELP Screen
Note on D5: Typical value for walking beam is 3
Note on D6: Enter total area of flocculator paddles in stage
Note on D7: Enter paddle stroke length
Note on D8: Enter volume of floccuation stage

## Database
Date & | [12 empty] | Current | Other | Current Dose | Other | Current Dose |  |  |  | Rapid Mix | Rapid Mix | Rapid Mix | Rapid Mix | Floc | Floc | Floc | Floc | Floc | Floc |  | Stock Solution Concentration |  |  | Raw Water | Jar 1 | Jar 1 | Jar 1 | Jar 1 | Jar 1 | Jar 1 | Jar 1 | Jar 1 | Jar 1 | Jar 1 | Jar 2 | Jar 2 | Jar 2 | Jar 2 | Jar 2 | Jar 2 | Jar 2 | Jar 2 | Jar 2 | Jar 2 | Jar 3 | Jar 3 | Jar 3 | Jar 3 | Jar 3 | Jar 3 | Jar 3 | Jar 3 | Jar 3 | Jar 3 | Jar 4 | Jar 4 | Jar 4 | Jar 4 | Jar 4 | Jar 4 | Jar 4 | Jar 4 | Jar 4 | Jar 4 | Jar 5 | Jar 5 | Jar 5 | Jar 5 | Jar 5 | Jar 5 | Jar 5 | Jar 5 | Jar 5 | Jar 5 | Jar 6 | Jar 6 | Jar 6 | Jar 6 | Jar 6 | Jar 6 | Jar 6 | Jar 6 | Jar 6 | Jar 6
Sample No. |  | Plant/Train | Water | Test | Test | Raw | Water | Water | Raw | Raw | Raw | Coagulant | Dose | Chemical 1 | Other | Chemical 2 | Other | Settled | IFE | Finished | Speed | Time | Speed | Time | Stage 1 | Stage 1 | Stage 2 | Stage 2 | Stage 3 | Stage 3 | Settle | Coagulant | Other | Other | Added to | Coagulant | Other Chem 1 | Other Chem 2 | Time to Floc | Floc | Settled | Settled | Filtered | Settled | Settled | Coagulant | Other Chem 1 | Other Chem 2 | Time to Floc | Floc | Settled | Settled | Filtered | Settled | Settled | Coagulant | Other Chem 1 | Other Chem 2 | Time to Floc | Floc | Settled | Settled | Filtered | Settled | Settled | Coagulant | Other Chem 1 | Other Chem 2 | Time to Floc | Floc | Settled | Settled | Filtered | Settled | Settled | Coagulant | Other Chem 1 | Other Chem 2 | Time to Floc | Floc | Settled | Settled | Filtered | Settled | Settled | Coagulant | Other Chem 1 | Other Chem 2 | Time to | Floc | Settled | Settled | Filtered | Settled | Settled | Last
38477.01 | Date | Name | Source | No. | Time | Turbidity | Temperature | Flow | pH | TOC | Alkalinity | Name | Coagulant | Name | Chemical 1 | Name | Chemical 2 | Turbidity | Turbidity | TOC | #1 | #1 | #2 | #2 | Speed | Time | Speed | Time | Speed | Time | Time |  | Chemical 1 | Chemical 2 | Jars | Dose | Dose | Dose | Formation | Size | Turb | pH | Turb | TOC | UV absorb | Dose | Dose | Dose | Formation | Size | Turb | pH | Turb | TOC | UV absorb | Dose | Dose | Dose | Formation | Size | Turb | pH | Turb | TOC | UV absorb | Dose | Dose | Dose | Formation | Size | Turb | pH | Turb | TOC | UV absorb | Dose | Dose | Dose | Formation | Size | Turb | pH | Turb | TOC | UV absorb | Dose | Dose | Dose | Floc | Size | Turb | pH | Turb | TOC | UV absorb | Column
# | m/d/y |  |  | # | hr:min | NTU | C | MGD | units | mg/L | mg/L | [9 empty] | RPM | min | RPM | min | RPM | min | RPM | min | RPM | min | min | % | % | % | mL | mg/L | mg/L | mg/L | min | mm | NTU | units | NTU | mg/L | cm-1 | mg/L | mg/L | mg/L | min | mm | NTU | units | NTU | mg/L | cm-1 | mg/L | mg/L | mg/L | min | mm | NTU | units | NTU | mg/L | cm-1 | mg/L | mg/L | mg/L | min | mm | NTU | units | NTU | mg/L | cm-1 | mg/L | mg/L | mg/L | min | mm | NTU | units | NTU | mg/L | cm-1 | mg/L | mg/L | mg/L | min | mm | NTU | units | NTU | mg/L | cm-1
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97
37044.01 | 2001-06-02 | Example | Wilson Lake | 1 | 9:00 | 6 | 15 | 7 | 7.4 | 4 | 65 | Alum | 20 | Cat Floc | 1 | Nalco 8109 | 0.05 | 2 | 0.15 | 2.2 | 100 | 60 |  |  | 40 | 15 | 30 | 15 | 15 | 15 | 10 |  |  |  |  | 10 | 2.5 | 0.05 | 4 | 0.5 | 4 | 7.3 | 0.15 | 3.8 | 0.07 | 20 | 3 | 0.1 | 3 | 0.5 | 3.8 | 7.2 | 0.14 | 3.7 | 0.065 | 30 | 3.5 | 0.15 | 2 | 1 | 3.5 | 7.1 | 0.13 | 3.5 | 0.06 | 40 | 4 | 0.2 | 1 | 2 | 3 | 7 | 0.12 | 3.3 | 0.055 | 50 | 4.5 | 0.25 | 1 | 2 | 2.8 | 6.9 | 0.1 | 3.2 | 0.05 | 60 | 5 | 0.3 | 1 | 2 | 3.5 | 6.8 | 0.14 | 3 | 0.04
37559.01 | 2002-10-30 | Thibodaux WTP | Bayou Lafourche | 1 | 2:00 | 53 | 23.7 | 1.44 | 7 | 7.7 | 72 | Alum | [8 empty] | 5 | 100 |  |  | 40 | 25 |  |  |  |  | 10 | 2 |  |  | 2000 | [5 empty] | 47.1 | 6.85 |  |  |  | 20 |  |  | 10 |  | 45.8 | 6.85 |  |  |  | 40 |  |  | 2 |  | 14.4 | 6.75 |  |  |  | 60 |  |  | 2 |  | 1.38 | 6.67 |  |  |  | 80 |  |  | 2 |  | 1.74 | 6.57 |  |  |  | 100 |  |  | 2 |  | 2.06 | 6.49
37685.01 | 2003-03-05 | Winchester WTP | Kentucky River | 1 | 15:00 | 9.9 | 6 | 2.5 | 7.7 |  | 122 | Thermafloc | [8 empty] | 80 | 100 |  |  | 52 | 14 | 15 | 14 |  |  | 15 | 2 |  |  | 2000 | 10 |  |  |  |  | 10.2 | 7.35 |  |  | 0.0755 | 20 |  |  |  |  | 4.2 | 7.15 |  |  | 0.064 | 30 |  |  |  |  | 3 | 7.19 |  |  | 0.058 | 40 |  |  |  |  | 3.2 | 7.16 |  |  | 0.053 | 50 |  |  |  |  | 0.8 | 7.29 |  |  | 0.052 | 60 |  |  |  |  | 1.45 | 7.12 |  |  | 0.0445
38477.01 | 2005-05-05 | Algiers WTP | Mississippi River | 1 | 0:00 |  | 20 | 10 |  |  |  | Ferric Sulfate | 7.25 | Magnafloc | 6.9 | Lime | 55 |  |  |  | 47 | 33 | 118 | 2 | 45 | 44 | [5 empty] | 0.15 | 0.15 | 1.5 | 1500 |  | 6.9 | 55 | [7 empty] | 3 | 6.9 | 55 | [7 empty] | 6 | 6.9 | 55 | [7 empty] | 7.25 | 6.9 | 55 | [7 empty] | 9 | 6.9 | 55 | [7 empty] | 12 | 6.9 | 55